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PART 1 - GENERAL
1.1 SUMMARY
Provide, install, configure where applicable, test and commission the industrial fiber-optic transmission system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.
1.2 BASIS OF DESIGN
Basis-of-design manufacturer and product: KBC Networks FCHA1. Source description: One Channel Video with ‘Up the Coax’ Telemetry.
Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.
1.3 SUBMITTALS
Manufacturer technical data sheet identifying the exact model and selected hardware variant.
Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.
Power calculation confirming input-supply compatibility and the total connected load where applicable.
Mounting, environmental and configuration details applicable to the proposed installation.
1.4 QUALITY ASSURANCE
Installation shall be performed by personnel familiar with industrial fiber-optic transmission, optical power budgets, connector and wavelength selection, signal interfacing and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.
PART 2 - PRODUCTS
2.1 REQUIRED PRODUCT
The equipment shall be KBC Networks FCHA1, or an approved equivalent meeting all requirements below. It shall be supplied as one channel video with ‘up the coax’ telemetry.
2.2 PRODUCT DESCRIPTION
The KBC FCHA1 series uses the most advanced digital technologies to provide excellent repeatable performance for today’s CCTV systems. It supports transmission of one video channel, one ‘Up the Coax’ data channel and two duplex contact closure channels over one multimode or singlemode optical fiber. PAL, NTSC and SECAM video standards are fully supported. The plug-and-play design ensures ease of installation with no electrical or optical adjustment needed. LED indicators are provided to clearly display the operational status of the unit. The series is available in wall-mount and 3U chassis card.
2.3 KEY FEATURES
10 bit digitally-encoded, non-compressed video transmission
Dual module 3U chassis card
Compatible with all major ‘Up the Coax’ manufacturers’ equipment
2 full duplex contact closure channels
2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS
	Requirement
	Specified performance

	Video - No. of Channels
	1

	Power - Power Input
	Wall-mount 12-24 Vac/dc @ 400mA

	Video - Format
	PAL / NTSC / SECAM

	Power - Power Supply for wall-mount (2)
	Input: 100 ~ 240 Vac Output: +12 Vdc UL and cUL listed PSU

	Video - Input/Output
	1.0V pk-pk typical, 75Ω

	Video - Bandwidth
	5 Hz ~ 6.5 MHz

	Video - Digital Encoding (non compressed)
	10 bit

	Power - Chassis Card
	Supplied from FR3 PSU

	Video - Differential Gain (10-90% APL)
	<2.0%

	Video - Differential Phase (10-90% APL)
	<2.0°

	Video - SNR
	>60dB

	Environmental - Operating Temperature
	-40°~+74°C / -40°~+165°F

	Environmental - Storage Temperature
	-40°~+74°C / -40°~+165°F

	Environmental - Operating Humidity
	0 to 95% non-condensing

	Data(1) - Data Formats
	Up the Coax

	Environmental - Mean Time Between Failure (MTBF)
	>100,000 Hours

	Data(1) - One way Channel
	1

	Data(1) - Two Way Channels
	1

	Mechanical - Dimensions (Wall-mount L x W x H)(7)
	155mm x 90mm x 36mm (6.1” x 3.45” x 1.42”)

	Mechanical - Number of 3U Chassis Card Slot(3)
	1

	Contact Closure - No. of duplex Channels
	2

	Contact Closure - Response Time
	500μs

	Contact Closure - Output
	SPST Relay, Normally Open

	Connectors - Video
	BNC

	Contact Closure - Switch Rating
	1A @ 30 Vdc max, 0.5A @ 125 Vac max

	Connectors - Contact Closure
	Screwblock Terminal

	Connectors - Fiber
	ST, SC or FC (ST fitted as standard)

	Optical - Wavelength
	1310nm / 1550nm

	Connectors - Power(4)
	Wall-mount Screw Block Terminal

	Optical - Fiber
	Multimode or Singlemode

	Optical - Number of Fibers
	1

	DIP Switch Settings - Telemetry Selection
	On / Off


The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.
2.5 SOURCE VERIFICATION NOTE
The requirements in this document have been prepared from specsheet-fcha1_series-low-rev1108a.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.
PART 3 - EXECUTION
3.1 EXAMINATION
Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.
Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.
Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.
Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.
3.2 INSTALLATION
Confirm signal type, channel count, direction, connector, wavelength, fiber type and link distance for every optical path.
Confirm compatible transmitter, receiver, card, chassis and power-supply arrangements before installation.
Protect and route fiber in accordance with the approved drawings, maintaining bend radius and connector cleanliness.
Label all electrical interfaces, optical links, fibers, cards, chassis positions and power circuits.
3.3 CONFIGURATION AND COMMISSIONING
Verify operation of every electrical signal and optical path included in the system.
Measure or otherwise confirm optical link performance and verify that the installed loss is within the approved budget.
Demonstrate alarm, redundancy and recovery functions where supported.
Provide final channel schedules, optical test results and installed model/serial information.
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