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ARCHITECTURAL AND ENGINEERING SPECIFICATION
Industrial Fiber-Optic Transmission System
Basis of Design: KBC Networks FTDB
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PART 1 - GENERAL
1.1 SUMMARY
Provide, install, configure where applicable, test and commission the industrial fiber-optic transmission system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.
1.2 BASIS OF DESIGN
Basis-of-design manufacturer and product: KBC Networks FTDB. Source description: Multi-Drop Bus Fiber Optic Modem.
Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.
1.3 SUBMITTALS
Manufacturer technical data sheet identifying the exact model and selected hardware variant.
Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.
Power calculation confirming input-supply compatibility and the total connected load where applicable.
Mounting, environmental and configuration details applicable to the proposed installation.
1.4 QUALITY ASSURANCE
Installation shall be performed by personnel familiar with industrial fiber-optic transmission, optical power budgets, connector and wavelength selection, signal interfacing and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.
PART 2 - PRODUCTS
2.1 REQUIRED PRODUCT
The equipment shall be KBC Networks FTDB, or an approved equivalent meeting all requirements below. It shall be supplied as multi-drop bus fiber optic modem.
2.2 PRODUCT DESCRIPTION
The KBC FTDB and FTD series products provide an optical bus network for RS-232, RS-422 or RS-485 data interfaces over one
2.3 KEY FEATURES
Multi-protocol data interface
Switchable termination and biasing
Multimode and singlemode
Wall-mount, DIN and 3U chassis card
2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS
	Requirement
	Specified performance

	Data(1) - Data Formats
	RS232, RS422, RS485 (2W & 4W)

	Environmental - Operating Temperature
	-40°~+74°C / -40°~+165°F

	Environmental - Storage Temperature
	-45°~+74°C / -40°~+165°F

	Data(1) - Number of Two-way Channels
	1

	Environmental - Operating Humidity
	0 to 95% non-condensing

	Data(1) - RS-232 Data Rate
	300 bps ~ 115.2 kbps

	Environmental - Mean Time Between Failure (MTBF)
	>100,000 Hours

	Data(1) - RS-422/485 Data Rate
	300 bps ~ 230 kbps

	Data(1) - Bit error rate
	<1 x 10-12

	Data(1) - Encoding schemes
	Manchester, Bi-Phase, NRZ, NRZI

	Mechanical - Dimensions (L x W x H)(5)
	70mm x 61mm x 44mm (2.76” x 2.40” x 1.73”) (Wall-mount & DIN Rail)

	Data(1) - Maximum Access Nodes
	128

	Mechanical - Number of 3U Chassis Card Slot(3)
	FTD: 1 slot FTDB: 2 slots

	Optical - Wavelength
	1310 / 1550nm

	Optical - Fiber
	Multimode or Singlemode

	Optical - Number of Fibers
	1 or 2 (between each unit)

	Connectors - Data
	4 way Screw Block Terminal

	Connectors - Fiber
	ST, SC or FC (ST fitted as standard)

	Power - Power Input
	(Wall-mount & DIN Rail) 12-24 Vac/dc

	Connectors - Power(4)
	Screw Block Terminal

	Power - Power Supply(2)
	Input: 100 ~ 240 Vac Output: +12 Vdc UL and cUL listed PSU

	DIP Switch Settings - Data(5)
	Switch selectable

	Power - Chassis Card
	Supplied from FR3 PSU

	DIP Switch Settings - 120Ω termination
	On / Off

	DIP Switch Settings - Biasing
	On / Off


The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.
2.5 SOURCE VERIFICATION NOTE
The requirements in this document have been prepared from specsheet-ftdb_series-low-rev1208.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.
PART 3 - EXECUTION
3.1 EXAMINATION
Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.
Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.
Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.
Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.
3.2 INSTALLATION
Confirm signal type, channel count, direction, connector, wavelength, fiber type and link distance for every optical path.
Confirm compatible transmitter, receiver, card, chassis and power-supply arrangements before installation.
Protect and route fiber in accordance with the approved drawings, maintaining bend radius and connector cleanliness.
Label all electrical interfaces, optical links, fibers, cards, chassis positions and power circuits.
3.3 CONFIGURATION AND COMMISSIONING
Verify operation of every electrical signal and optical path included in the system.
Measure or otherwise confirm optical link performance and verify that the installed loss is within the approved budget.
Demonstrate alarm, redundancy and recovery functions where supported.
Provide final channel schedules, optical test results and installed model/serial information.
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