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ARCHITECTURAL AND ENGINEERING SPECIFICATION
Industrial Ethernet Media Converter
Basis of Design: KBC Networks MCG1-P2
	Product family: Industrial Ethernet media conversion equipment
	Document status: Tender / design specification

	Source data: specsheet-mcg1-p2_series-low--rev1405.pdf
	Prepared: 4 August 2026



PART 1 - GENERAL
1.1 SUMMARY
Provide, install, configure where applicable, test and commission the industrial ethernet media converter described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.
1.2 BASIS OF DESIGN
Basis-of-design manufacturer and product: KBC Networks MCG1-P2. Source description: MCG1-P Series 10/100/1000 Ethernet Media Converter with SFP Port.
Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.
1.3 SUBMITTALS
Manufacturer technical data sheet identifying the exact model and selected hardware variant.
Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.
Power calculation confirming input-supply compatibility and the total connected load where applicable.
Mounting, environmental and configuration details applicable to the proposed installation.
1.4 QUALITY ASSURANCE
Installation shall be performed by personnel familiar with industrial Ethernet, copper and optical interfaces, PoE power budgeting, transceiver selection and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.
PART 2 - PRODUCTS
2.1 REQUIRED PRODUCT
The equipment shall be KBC Networks MCG1-P2, or an approved equivalent meeting all requirements below. It shall be supplied as mcg1-p series 10/100/1000 ethernet media converter with sfp port.
2.2 PRODUCT DESCRIPTION
The KBC MCG1-P series is a fully ruggedized 10/100/1000 Ethernet media converter. It supports transmission of an Ethernet channel
The MCG1-P Series is available as a compact, wall-mount unit.
2.3 KEY FEATURES
IEEE802.3ab 1000Base-T compliant
10/100/1000 auto-sensing
MDI/MDIX
Ultra-compact footprint
SFP interface
Wide operational temperature range
2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS
	Requirement
	Specified performance

	Standards - IEEE Standard
	IEEE 802.3 10BASE-T IEEE 802.3u 100BASE-TX IEEE 802.3ab 1000BASE-T IEEE 802.3z 1000BASE-X Fiber IEEE 802.3x Full duplex

	Environmental - Operating Temperature
	-40° ~ +70°C / -40° ~ +158°F

	Environmental - Storage Temperature
	-40° ~ +70°C / -40° ~ +158°F

	Environmental - Operating Humidity
	0 to 95% non-condensing

	Environmental - Mean Time Between Failure (MTBF)
	>100,000 Hours

	Data - Data Formats
	Ethernet

	Mechanical - Dimensions (W x H x D)
	77mm × 70mm × 44mm

	Data - Two Way Channels
	1

	Mechanical - Compact unit
	(3.03” x 2.76” x 1.73”)

	Data - Data Rate
	10/100/1000Mbps auto-sensing half & full duplex

	Connectors - Ethernet
	1 x RJ45

	Power - Power Input
	12-24 Vac/dc

	Connectors - Fiber
	SFP

	Power - Power Supply (1)
	Input: 100 ~ 240 Vac Output: +12 Vdc

	Connectors - Power(2)
	Screw block terminal


The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.
2.5 SOURCE VERIFICATION NOTE
The requirements in this document have been prepared from specsheet-mcg1-p2_series-low--rev1405.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.
PART 3 - EXECUTION
3.1 EXAMINATION
Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.
Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.
Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.
Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.
3.2 INSTALLATION
Confirm copper speed, duplex mode, optical speed, connector, wavelength, fiber type and link distance for each connection.
Provide approved fixed-optic or SFP transceivers matched to the intended optical path.
Provide compatible power, protective earthing, cable management and environmental protection.
Label each converter, power circuit, copper port and optical link to match the project documentation.
3.3 CONFIGURATION AND COMMISSIONING
Verify link operation on every connected copper and optical interface.
Verify PoE negotiation and delivered power at each powered device where applicable.
Confirm speed, duplex, link-fault and diagnostic behaviour supported by the selected model.
Provide final link schedules, test results and installed model/serial information.
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