KBC MOBILE SURVEILLANCE SYSTEM (MSS)

PART 1 - GENERAL

1.1 SUMMARY

Provide, install, configure (where applicable), test, and commission the industrial power solution described in this specification, including the required interfaces, power connections, mounting hardware, and compatible accessories.

1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks MSS. Source description: Mobile Surveillance System.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial DC power systems, load calculations, battery or solar sizing, protective devices, environmental enclosures and applicable electrical practices. Verify all product capabilities from the current manufacturer data sheet and selected part number.

PART 2 - PRODUCTS

2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks MSS, or an approved equivalent meeting all requirements below. It shall be supplied as a mobile surveillance system.

2.2 PRODUCT DESCRIPTION

Mobile Surveillance Systems (MSS) are self-contained solutions for monitoring locations that lack infrastructure, require time-sensitive deployment, are temporary or a combination of these factors. They are compact, rugged, and easy to operate. MSS units consist of a base unit with on-board solar panel(s), a charge controller and batteries (purchased separately), along with power and network connections for all connected devices. A removable quick-connect pod provides a mounting platform for cameras, wireless, radar or other systems.

MSS units are a force multiplier for management, security, medical, law enforcement or event personnel by providing the ability to monitor an area more efficiently and effectively. The systems are most effective when used in groups, as they can be easily linked together in perimeter, star, and linear configurations. Because of their size and maneuverability, MSS units provide a platform that can be deployed quickly in smaller areas and is less conspicuous than other solutions.

MSS-KT-300-15 operates in a variety of weather environments and includes multiple security features.

2.3 KEY FEATURES

Compact self-contained unit – maneuverable and easy to deploy

Industrial – vandal-resistant – low maintenance

Remote, mobile, cost-effective

Unique gas shock-assisted mast lift assembly – elevation up to 15 feet

Removable quick-connect interchangeable pods

Adjustable solar panel – gas shock-assisted lift deployable at multiple angles

MPPT Charge controller

Space for up to 3 x 110 Ah batteries in base (purchased separately)

Optional configurations and accessories are available

2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Mechanical | MSS-KT-300-15 |
| Stowed | 32” x 41” x 65” |
| Deployed | 63” x 68” x 180” |
| Shipping Weight | 400 lb (620 lb with batteries) |
| Construction | Steel Chassis |
| Mast | Swing-Arm Gas Spring Assist - Aluminum |
| Steel/Aluminum Chassis | Swing-Arm gas spring-assisted mast (1x 80 lb and 1x 60 lb) / 4x 10” pneumatic tires with steel hub with 300 lb capacity / 4x Adjustable outriggers and levelers / spring-assisted solar array (2x 60 lb) |
| Wheels | 10” Pneumatic Tire/Steel Hub (4x) 300 lb Capacity Each |
| Supports | 4 Adjustable Outriggers & Levelers |
| Electronics Tray | Fixed aluminum tray |
| Solar Mount | Adjustable with Pin Lock |
| Mast Lift Mechanism | 1 – 80 lb & 1 - 60 lb Gas Spring |
| Solar Lift Mechanism | 2 – 60 lb Gas Springs |
| Quick-Connect Pod | Aluminum w/ 12VDC & RJ45 Connector |
| Finish | Powder Coat - White |
| Security Features - Base | 2x Key Lock/Removable Wheels |
| Security Features - Mast | Key Lock Latches |
| Security Features - Quick-Connect Pod | Key Lock Latch |
| Power - Electrical | 12VDC System |
| Power - Batteries | 3x – 110 Ah |
| Power - Solar Panels | 3x - 100W Panels |
| Power - Wiring | Cat6e & 14 GWA 2-wire Internal to Mast & Base |
| Power - Charge Controller | MPPT 100/20 - Bluetooth Capable |
| Quick-Connect Pod - Latches | Standard & Key Lock |
| Quick-Connect Pod - Wiring | Cat6e/18 GWA 2-wire |
| Quick-Connect Pod - Weatherproofing | Square Rubber “O” Ring, Rubber Gasket |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from MSS_Series-Specification_Sheet-2303.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

PART 3 - EXECUTION

3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

3.2 INSTALLATION

Confirm the continuous and peak load, input source, output voltage, required autonomy and environmental conditions.

Verify battery, solar-array, charger, controller, inverter or DC distribution compatibility where applicable.

Provide protective earthing, overcurrent protection, isolation, cable sizing and weatherproof entry arrangements.

Install all equipment, enclosures and mounting assemblies in accordance with manufacturer instructions and approved drawings.

3.3 CONFIGURATION AND COMMISSIONING

Verify input, charging, output voltage, and load performance under normal operating conditions.

Verify battery autonomy, solar charging or UPS transfer operation where applicable.

Demonstrate alarm, recovery and protection functions supported by the selected system.

Provide final power calculations, settings, test results and installed model/serial information.